Master FC400
MFC 125
INPUT		
Voltage	380 / 400 / 415 V three-phase 	
Voltage tolerance	400 V ±20% @ full load 	
Frequency tolerance	45 ÷ 65 Hz	
Current distorsion	<5% C (HC Version)	
Soft start	0 - 100% in 120 sec. configurable	
OUTPUT and INVERTER OUTPUT		
Rated power	125000 VA	
Active power	100000 W	
Number phases	3 	
Crest factor (Ipeak/Irms)	3 : 1 	
Waveform	sinusoidal 	
Static stability	±1% 	
Dynamic stability	±5% 	
Frequency	400 Hz 	
Voltage distortion with non-linear load	<4% 	
Voltage distortion with linear load	<3% 	
Overload	110% for 60 min.; 125% for 10 min.; 150% for 1 min. 	
ENVIRONMENTAL		
Color	Light gray RAL 7035 	
Communication	Double RS232 + remote contacts + 2 slots for communications interface 	
Protection rating	IP20 	
AC/AC efficiency	up to 92% 	
Noise (at 1 m)	72 dBA  	
Operating temperature	0 °C - 40 °C (50°C @ 75% load)	
Relative humidity	5-95% non-condensing	
Standards	European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	590 kg	
Dimensions (h w d)	1900 x 800 x 800  mm