CSS Sentryum
CSS CBM 6
INPUT		
Voltage	380 / 400 / 415 V three-phase + N - 220 / 230 / 240 V single-phase + N 	
Voltage tolerance	230 / 400 V ±20% @ full load (for wider tolerance conditions apply) 	
Frequency tolerance	40 - 72 Hz	
Power factor	≥0.99	
BY PASS		
Rated voltage	220 / 230 / 240 V single-phase + N	
Voltage tolerance	From 180 V (adjustable 180-200) to 264 V (adjustable 250-264)  	
Rated frequency	50 or 60 Hz 	
Frequency tolerance	±5% (selectable) 	
Number phases	1 + N 	
OUTPUT and INVERTER OUTPUT		
Rated power	6000 VA	
Active power	6000 W	
Power according with EN 50171	5000 VA / W 	
Rated voltage	220 / 230 / 240 V single-phase + N 	
Number phases	1 + N 	
Crest factor (Ipeak/Irms)	3 : 1 	
Waveform	Sinusoidal 	
Static stability	±0.5% 	
Dynamic stability	EN 62040-3 class performance 1 non-linear load 	
Frequency	50 or 60 Hz (ajustable) 	
Voltage distortion with non-linear load	≤1.5% 	
Voltage distortion with linear load	<1% 	
BATTERIES		
Type	VRLA - 10 YEARS expected lifespan 	
Type of charging	One level, Two level, Cyclic recharge (selectable) 	
ENVIRONMENTAL		
Color	RAL 7016 Anthracite grey 	
Communication	Status led – Color graphic touch screen display - 2 communication interface slots – USB -RS232 - 4 relay outputs - 5 opto-isolated input 	
Protection rating	IP20 	
Line-Interactive/Smart Active efficiency	Up to 99% 	
Noise (at 1 m)	<40 [dBA ±2] (SMART ACTIVE) 	
Remote signals	voltage free contacts	
Operating temperature	0 °C - +40 °C	
Relative humidity	5-95% non-condensing	
Standards	EN 50171 - European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	102 kg	
Dimensions (h w d)	1320x440x840 mm