Multi Power2 Scalable
M2S 1000 PC0
OVERALL SPECIFICATION		
Cabinet type	M2S 1000 PC0 Power Cabinet 	
Power Module nominal power (Named PM)	67 kW	
Solution nominal Power	1000 kW	
Output power factor [pf]	1 	
Parallelable (up to)	4 	
Cabinet layout description	Up to 16 x MP2 67 PM BLUE or 16 x MP2 67 PM. Unit without switches. 	
INPUT		
Rated power	1000000 VA	
Voltage	380 / 400 / 415 V three-phase + N  	
Frequency tolerance	40 - 72 Hz	
Power factor	0.99	
BY PASS		
Rated voltage	380 / 400 / 415 V three-phase + N	
Voltage tolerance	From 180 V (adjustable 180-200) to 264 V (adjustable 250 – 264) referring to neutral (Ph-N) 	
Rated frequency	50 or 60 Hz (selectable) 	
Frequency tolerance	± 5% (selectable) 	
Number phases	3 + N 	
OUTPUT and INVERTER OUTPUT		
Rated power	1000000  VA	
Active power	1000000  W	
Number phases	3 + N 	
Output Voltage	380 / 400 / 415 V three-phase + N  	
Waveform	Sinewave 	
Dynamic stability	EN62040-3 class performance 1 non-linear load  	
Frequency	50 or 60 Hz 	
Overload	125% for 10 min.; 150% for 1 min. 	
BATTERIES		
Type	VRLA AGM / GEL; NiCd; Li-Ion; Supercaps 	
Type of charging	One level, Two level, Cyclic recharge (selectable) 	
ENVIRONMENTAL		
Color	RAL 9005 	
Communication	10” Graphic touch screen display – UPS Status led bar – 3 slots for communication interface, 10 input and 8 output signals 	
Protection rating	IP20 finger proof (either with cabinet doors open or close)  	
AC/AC efficiency	Up to 98.1% with MP2 67 PM BLUE (ON LINE mode) 	
Operating temperature	0 °C - +40 °C	
Relative humidity	5-95% non condensing	
Standards	European directives: LV 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive & Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111  	
DATA		
Weight including PMs to reach nominal power	1949 kg	
Dimensions (h w d)	2000 x 2400 x 1025 mm	
Input phases	3 	
Output phases	3