Multi Power2
MP2 300 PCM
OVERALL SPECIFICATION		
Cabinet type	MP2 300 PCM Power Cabinet 	
Power Module nominal power (Named PM)	67 kW	
Solution nominal Power	300 kW	
Output power factor [pf]	1 	
Parallelable (up to)	4 	
Cabinet layout description	Up to 5 x MP2 67 PM BLUE or 5 x MP2 67 PM. Unit with manual bypass switch. 	
INPUT		
Rated power	300000 VA	
Voltage	380 / 400 / 415 V three-phase + N 	
Frequency tolerance	40 - 72 Hz	
Power factor	0.99	
BY PASS		
Rated voltage	380 / 400 / 415 V three-phase + N	
Voltage tolerance	From 180 V (adjustable 180-200) to 264 V (adjustable 250 – 264) referring to neutral (Ph-N)  	
Rated frequency	50 or 60 Hz (selectable) 	
Frequency tolerance	± 5% (selectable) 	
Number phases	3 + N  	
OUTPUT and INVERTER OUTPUT		
Rated power	300000 VA	
Active power	300000 W	
Number phases	3 + N 	
Output Voltage	380 / 400 / 415 V three-phase + N 	
Waveform	Sinewave 	
Dynamic stability	EN62040-3 class performance 1 non-linear load 	
Frequency	50 or 60 Hz 	
Overload	125% for 10 min.; 150% for 1 min. 	
BATTERIES		
Type	VRLA AGM / GEL; NiCd; Li-Ion; Supercaps  	
Type of charging	One level, Two level, Cyclic recharge (selectable) 	
ENVIRONMENTAL		
Color	RAL 9005  	
Communication	10” Graphic touch screen display – UPS Status led bar – 2 slots for communication interface, 5 input, 4 output signals and embedded NetMan 208 	
Protection rating	IP20 finger proof (either with cabinet doors open or close) 	
AC/AC efficiency	Up to 98.1% with MP2 67 PM BLUE (ON LINE mode) 	
Operating temperature	0 °C - +40 °C	
Relative humidity	5-95% non condensing	
Standards	European directives: LV 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive & Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight including PMs to reach nominal power	429 kg	
Dimensions (h w d)	1995 x 600 x 940  mm	
Input phases	3 	
Output phases	3